## Required Info
class | must ask* | class | optional
HVACTemplate:Thermostat | Heating Setpoint Schedule | HVACTemplate:System:VAV | Supply Fan Total Efficiency
| Cooling Setpoint Schedule |  | Cooling Coil Type
HVACTemplate:System:VAV | System Availabilily Schedule |  | Cooling Coil Design Setpoint
| Minimum Outdoor Air Schedule Name |  | Heating Coil Type
HVACTemplate:Plant:ChilledWaterLoop | Condenser Water Temperature Control Type |  | Heating Coil Design Setpoint
HVACTemplate:Plant:Chiller | Chiller Type |  | Preheat Coil Type
| Nominal COP |  | Economizer Type
HVACTemplate:Plant:Boiler | Boiler Type |  | Supply Fan Placement
HVACTemplate:Plant:Tower | Tower Type |  | Cooling Coil Setpoint Reset Type
Heating Coil Setpoint Reset Type
Dehumidification Control Type
Humidifier Type
Sizing Option
|  | HVACTemplate:Zone:VAV | Reheat Coil Type
Damper Heating Action
Baseboard Heating Type
|  | HVACTemplate:Plant:ChilledWaterLoop | Pump Control Type
Chilled Water Setpoint Schedule Name OR Chilled Water Design Setpoint
Condenser Water Setpoint Schedule Name OR Condenser Water Design Setpoint
Chilled Water Setpoint Reset Type
Fluid Type
|  | HVACTemplate:Plant:Chiller | Condenser Type
|  | HVACTemplate:Plant:HotWaterLoop | Pump Control Type
Hot Water Plant Operation Scheme Type
Hot Water Design Setpoint
Hot Water Pump Configuration
Hot Water Setpoint Reset Type
Hot Water Pump Type
|  | HVACTemplate:Plant:Boiler | Fuel Type
*must-have or not are separated based on whether the variable has a default value or not

## ThermoStat
HVACTemplate:Thermostat | Unit | Must Have or not | Current Input Value | Note
Name |  | Y | Main Thermostat | Name
Heating Setpoint Schedule Name* |  | Y (One of these) | Annual Thermo Plan | Heating
Constant Heating Setpoint | C
Cooling Setpoint Schedule Name* |  | Y (One of these) | Annual Thermo Plan | Cooling
Constant Cooling Setpoint | C
* Setpoint Schedules are Schedule:Compact type object. Below are heating and cooling setpoint samples
Cooling Schedule Sample |  |  | Heating Schedule Sample
Field | Obj |  | Field | Obj
Name | School Cooling Setpoints |  | Name | School Heating Setpoints
Schedule Type Limits Name | Temperature |  | Schedule Type Limits Name | Temperature
Field 1 | Through: 12/31 |  | Field 1 | Through: 12/31
Field 2 | For: Weekdays |  | Field 2 | For: Weekdays
Field 3 | Until: 06:00 |  | Field 3 | Until: 06:00
Field 4 | 30 |  | Field 4 | 6
Field 5 | Until: 22:00 |  | Field 5 | Until: 22:00
Field 6 | 25 |  | Field 6 | 25
Field 7 | Until: 24:00 |  | Field 7 | Until: 24:00
Field 8 | 30 |  | Field 8 | 6
Field 9 | For: Saturday |  | Field 9 | For: Saturday
Field 10 | Until: 06:00 |  | Field 10 | Until: 06:00
Field 11 | 30 |  | Field 11 | 6
Field 12 | Until: 18:00 |  | Field 12 | Until: 18:00
Field 13 | 25 |  | Field 13 | 25
Field 14 | Until: 24:00 |  | Field 14 | Until: 24:00
Field 15 | 30 |  | Field 15 | 6
Field 16 | For: Sunday Holidays AllOtherDays |  | Field 16 | For: Sunday Holidays AllOtherDays
Field 17 | Until: 24:00 |  | Field 17 | Until: 24:00
Field 18 | 33 |  | Field 18 | 6

## System
HVACTemplate:System:VAV | Unit | Must Have or not | Current Input Value | Note | Comment | *Schedule:Compact type object. Below are used values
Name |  | Y | VAV with Reheat | Name
System Availabilily Schedule Name |  | Y | School HVAC* |  | in the predefined schedule, 1.0 means on | HVAC Schedule Sample |  | Minimum OA Schedule Sample
Supply Fan Maximum Flow Rate |  | Y | autosize | Supply Fan | autosize -> sum of the zone air flow rate | Field | Obj | Field | Obj
Supply Fan Minimum Flow Rate | m3/s | Y | autosize |  |  | Name | School HVAC | Name | School Minimum OA
Supply Fan Total Efficiency | m3/s | Y | 0.7 |  | product of te motor efficiency and the impeller efficiency*; 0.7 is default value | Schedule Type Limits Name | on/off | Schedule Type Limits Name | on/off
Supply Fan Delta Pressure | Pa | Y | 1000 |  | pressure rise at full flow and 20 C at sea level, 101325 Pa | Field 1 | Through: 12/31 | Field 1 | Through: 12/31
Supply Fan Motor Efficiency |  | Y | 0.9 |  | equals to (shaft power / electrical power consumed) | Field 2 | For: Weekdays | Field 2 | For: Weekdays
Supply Fan Motor in Air Stream Fraction |  | Y | 1 |  | the fraction of the motor heat that is added to the air stream | Field 3 | Until: 06:00 | Field 3 | Until: 07:00
Cooling Coil Type |  | Y | ChilledWater | Cooling Coil | can choose from ChilledWater; ChilledWaterDetailedFlatModel (a self-defined object) | Field 4 | 0 | Field 4 | 0
Cooling Coil Availability Schedule Name |  |  |  |  | usually left blank to allow cooling coil to be available anytime | Field 5 | Until: 22:00 | Field 5 | Until: 22:00
Cooling Coil Setpoint Schedule Name |  | Y (one of these) |  |  | controls the supply air temperature delivered to the zone | Field 6 | 1 | Field 6 | 1
Cooling Coil Design Setpoint | C |  | 13 |  | constant cooling supply air setpoint temperature | Field 7 | Until: 24:00 | Field 7 | Until: 24:00
Heating Coil Type |  | Y | HotWater | Heating Coil | can choose from HotWater; Electric; Gas; None | Field 8 | 0 | Field 8 | 0
Heating Coil Availability Schedule Name |  |  |  |  | same as cooling | Field 9 | For: Saturday | Field 9 | For: Saturday
Heating Coil Setpoint Schedule Name |  | Y (one of these) |  |  |  | Field 10 | Until: 06:00 | Field 10 | Until: 07:00
Heating Coil Design Setpoint | C |  | 7.2 |  |  | Field 11 | 0 | Field 11 | 0
Gas Heating Coil Efficiency |  | Y | 0.8 |  | gas burner efficiency | Field 12 | Until: 18:00 | Field 12 | Until: 18:00
Gas Heating Coil Parasitic Electric Load | W |  |  |  | parasitic electric load associated with gas heating operation | Field 13 | 1 | Field 13 | 1
Preheat Coil Type |  | Y | None | Preheat Coil (either preheat or heating) | can choose from HotWater; Electric; Gas; None (either heating or preheat - not both) | Field 14 | Until: 24:00 | Field 14 | Until: 24:00
Preheat Coil Availability Schedule Name | [5 empty] | Field 15 | 0 | Field 15 | 0
Preheat Coil Setpoint Schedule Name |  | Y (one of these) |  |  |  | Field 16 | For: Sunday Holidays AllOtherDays | Field 16 | For: Sunday Holidays AllOtherDays
Preheat Coil Design Setpoint | C |  | 10 |  |  | Field 17 | Until: 24:00 | Field 17 | Until: 24:00
Gas Preheat Coil Efficiency |  | Y | 0.8 |  |  | Field 18 | 0 | Field 18 | 0
Gas Preheat Coil Parasitic Electric Load | W
Maximum Outdoor Air Flow Rate | m3/s | Y | autosize | Outdoor Air Flow | autosize means 100% of full supply can be taken from outdoor air
Minimum Outdoor Air Flow Rate | m3/s | Y | autosize |  | autosize -> calculated by the outdoor air requirements of each zone
Minimum Outdoor Air Control Type |  | Y | ProportionalMinimum |  | can choose from FixedMinimum; Proportional Minimum
Minimum Outdoor Air Schedule Name |  | Y | School Minimum OA* |  | blank if same for all hours in entire year
Economizer Type |  | Y | FixedDryBulb | Economizer | can choose from NoEconomizer; FixedDryBulb; DifferentialDryBulb, etc
Economizer Lockout |  | Y | NoLockout |  | only has NoLockout choice for current version
Economizer Upper Temperature Limit | C |  |  |  | blank if no outdoor air temperature high limit control
Economizer Lower Temperature Limit | C |  |  |  | blank if no outdoor air temperature low limit control
Economizer Upper Enthalpy Limit | J/kg
Economizer Maximum Limit Dewpoint Temperature | C
Supply Plenum Name |  |  |  | Plenum | blank if none; if does, must be modeled as a zone
Return Plenum Name
Supply Fan Placement |  | Y | DrawThrough |  | can choose from DrawThrough; BlowThrough
Supply Fan Part-Load Power Coefficients |  | Y | InletVaneDampers |  | can choose from InletVaneDampers; OutletDampers; VariableSpeedMotor, etc.
Night Cycle Control |  | Y | StayOff | Night Cycle | control system behavior when 0.0 in schedule;
Night Cycle Control Zone Name |  |  |  |  | enter only when previous field is Cycle On Control Zone
Heat Recovery Type |  | Y | None | Heat Recovery | can choose from None; Sensible; Enthalpy
Sensible Heat Recovery Effectiveness |  | Y (one of these) | 0.7
Latent Heat Recovery Effectiveness |  |  | 0.65
Cooling Coil Setpoint Reset Type |  | Y | None | Coil Setpoint Reset | if None, use the Cooling Coil Setpoint Schedule/ Cooling Coil Design Setpoint
Heating Coil Setpoint Reset Type |  | Y | None |  | if None, use the Heating Coil Setpoint Schedule/ Cooling Coil Design Setpoint
Dehumidification Control Type |  | Y | None | Dehumidification | can choose from None; CoolReheat
Dehumidification Control Zone Name
Dehumidification Setpoint | percent
Humidifier Type |  | Y | None | Humidifier | can choose from None; EletricStream
Humidifier Availability Schedule Name
Humidifier Rated Capacity | m3/s
Humidifier Rated Electric Power | W
Humidifier Control Zone Name
Humidifier Setpoint | percent
Sizing Option |  | Y | NonCoincident | Sizing | sizes on sum of noncoincident zone design supply air flow rates
Return Fan |  |  |  | Return Fan | Yes or No choices; default is No
Return Fan Total Efficiency
Return Fan Delta Pressure | Pa
Return Fan Motor Efficiency
Return Fan Motor in Air Stream Fraction
Return Fan Part-Load Power Coefficients
* schedules defined on the right of this sheet
* motor efficiency = power to shaft / electrical power input to the motor
* impeller efficiency = (mass flow rate of air * pressure rise) / (shaft power * air density)

## Zone
HVACTemplate:Zone:VAV | Unit | Must Have or not | Current Input Value | Note | Comment
Zone Name |  | Y | ZONE ONE | Name | defined phyical model
Template VAV System Name |  | Y | VAV wit Reheat |  | a defined HVACTemplate:System:VAV type object
Template Thermostat Name |  | Y | Main Thermostat |  | a defined HVACTemplate:Therostat type object
Supply Air Maximum Flow Rate | m3/s | Y | autosize |  | automatically determined based on loads experienced by the zone during design days
Zone Heating Sizing Factor |  |  |  | Sizing Factor | if left blank, will use the number defined in Sizing:Parameters class
Zone Cooling Sizing Factor
Zone Minimum Air Flow Input Method |  | Y | Constant | Minimum Air Flow | decide how the program determine the minimum flow rate
Constant Minimum Air Flow Fraction |  | Y (one of these) | 0.2 |  | defined as a fraction of the maximum air flow rate
Fixed Minimum Air Flow Rate | m3/s
Minimum Air Flow Fraction Schedule Name
Outdoor Air Method |  | Y | Flow/Person | Outdoor Air
Outdoor Air Flow Rate per Person | m3/s | Y (one of these) | 0.0094 |  | 0.0094 is the default value (2 cfm per person)
Outdoor Air Flow Rate per Zone Floor Area | m3/s-m2
Outdoor Air Flow Rate per Zone | m3/s
Reheat Coil Type |  | Y | HotWater | Reheat | can choose from HotWater/Electric/Gas/None
Reheat Coil Availability Schedule Name |  |  |  |  | should be left blank if want reheat coil to be available for entire year
Damper Heating Action |  | Y | Reverse | Damper | can choose from Normal(constant)/Reverse(may increase above minimum air flow)
Maximum Flow per Zone Floor Area During Reheat | m3/s-m2 |  |  | Maximum Flow | maximum flow will not be limited if left blank
Maximum Flow Fraction During Reheat
Maximum Reheat Air Temperature | C |  |  |  | will not be limited if left blank
Design Specification Outdoor Air Object Name for Control |  |  |  |  | specifies a DesignSpecification:OutdoorAir object
Supply Plenum Name |  |  |  | Plenum
Return Plenum Name
Baseboard Heating Type |  | Y | None | Baseboard | can choose from HotWater/Electric/None
Baseboard Heating Availability Schedule Name
Baseboard Heating Capacity | W | Y | autosize
Zone Cooling Design Supply Air Temperature Input Method |  | Y | SystemSupplyAirTemperature | Zone Cooling & Heating | SystemSupplyAirTemperature will use info defined in Template VAV system
Zone Cooling Design Supply Air Temperature | C | (One of these if not choosing SystemSupplyAirTemperature
Zone Cooling Design Supply Air Temperature Difference | deltaC
Zone Heating Design Supply Air Temperature Input Method |  | Y | SupplyAirTemperature
Zone Heating Design Supply Air Temperature | C | Y | 50
Zone Heating Design Supply Air Temperature Difference | deltaC
Design Specification Outdoor Air Object Name for Sizing |  |  |  |  | specifies a DesignSpecification:OutdoorAir object
Design Specification Zone Air Distribution Object Name |  |  |  |  | specifies a DesignSpecification:ZoneAirDistribution object

## Plant-Chiller
HVACTemplate:Plant:ChilledWaterLoop | Unit | Must Have or not | Current Input Value | Note | Comment | Chiller serving ChilledWaterLoop | HVACTemplate:Plant:Chiller | Unit | Must Have or not | Current Input Value | Note | Comment
Name |  | Y | Chilled Water Plant | Name |  |  | Name |  | Y | Chiller 1 | Name
Pump Schedule Name |  |  |  | Pump Name and Type | blank if always available |  | Chiller Type |  | Y | ElectricReciprocatingChiller | Type | DistrictChilledWater/ ElectricCentrifugalChiller/ ElectricScrewChiller/ ElectricReciprocatingChiller
Pump Control Type |  | Y | Intermittent |  | continuous or intermittent (continuous needs a schedule) |  | Capacity | W | Y | autosize | Capacity | autosize -> based on pea loads during design days
Chiller Plant Operation Scheme Type |  | Y | Default | Chiller | can choose from default (makes all equip available at all time); userdefined; |  | Nominal COP | W/W | Y | 3.6 | COP | should not include energy use due to pumps, evap-cooled or air-cooled condenser fans, cooling tower fans
Chiller Plant Equipment Operation Schemes Name |  |  |  |  | include PlantEquipmentOperationSchemes only when previous field is userdefined |  | Condenser Type |  | Y | WaterCooled | Condenser | AirCooled/ WaterCooled (must have tower object)/ EvaporativelyCooled
Chilled Water Setpoint Schedule Name |  | Y (one of these) |  |  |  |  | Priority |  |  |  | Priority | used for Plant:ChilledWaterLoop - Chiller Plant Operation Scheme
Chilled Water Design Setpoint | C |  | 7.22 |  |  |  | Sizing Factor |  | Y | 1 | Sizing
Chilled Water Pump Configuration |  | Y | VariablePrimaryNoSecondary | Water Pump | define types of flow to chiller and to coils |  | Minimum Part Load Ratio |  |  |  | Ratio | default 0.0
Primary Chilled Water Pump Rated Head | Pa | Y | 179352 |  | rated head of the primary chilled water pump |  | Maximum Part Load Ratio |  | Y | 1
Secondary Chilled Water Pump Rated Head | Pa | Y | 179352 |  | field applicable only if "Chilled Water Pump Configuration" has one variable one constant |  | Optimum Part Load Ratio |  | Y | 1
Condenser Plant Operation Schemes Type |  | Y | Default | Condenser | can choose from default; UserDefined |  | Minimum Unloading Ratio |  | Y | 0.25
Condenser Equipment Operation Schemes Name |  |  |  |  | only if previous field is UserDefined |  | Leaving Chilled Water Lower Temperature Limit | C | Y | 5 | Limit | lower limit for the leaving chilled water temperature
Condenser Water Temperature Control Type |  | Y | SpecifiedSetpoint |  | can choose from OutdoorWetBulbTemperature; SpecifiedSetpoint
Condenser Water Setpoint Schedule Name |  | Y (one of these)
Condenser Water Design Setpoint | C |  | 29.4
Condenser Water Pump Rated Head | Pa | Y | 179352
Chilled Water Setpoint Reset Type |  | Y | None | Temperature Reset and Setpoint | can choose from None (use the schedule or setpoint); OutDoorAirTemperatureReset
Chilled Water Setpoint at Outdoor Dry-Bulb Low | C |  | 12.2 |  | chilled water setpoint when outdoor is at or below this limit
Chilled Water Reset Outdoor Dry-Bulb Low | C |  | 15.6 |  | when outdoor is at or below this limit, setpoint is value from above field
Chilled Water Setpoint at Outdoor Dry-Bulb High | C |  | 6.7 |  | chilled water setpoint when outdoor is at or above this limit
Chilled Water Reset Outdoor Dry-Bulb High | C |  | 26.7 |  | when outdoor is at or above this limit, setpoint is value from above field
Chilled Water Primary Pump Type |  | Y | SinglePump | Pump configuration
Chilled Water Secondary Pump Type |  | Y | SinglePump
Condenser Water Pump Type |  | Y | SinglePump
Chilled Water Supply Side Bypass Pipe |  | Y | Yes | Bypass Pipe | Yes/No;
Chilled Water Demand Side Bypass Pipe |  | Y | Yes
Condenser Water Supply Side Bypass Pipe |  | Y | Yes
Condenser Water Demand Side Bypass Pipe |  | Y | Yes
Fluid Type |  | Y | Water | Fluid | Water/ EthyleneGlycol/Propylene
Loop Design Delta Temperature | deltaC | Y | 6.67 |  | temperature difference used in sizing the loop flow rate
Minimum Outdoor Dry Bulb Temperature | C
Chilled Water Load Distribution Scheme |  | Y | SequentialLoad | Load Distribution Scheme | Optimal/ SequentialLoad/ UniformLoad/ SequentialUniformPLR/ UniformPLR
Condenser Water Load Distribution Scheme |  | Y | SequentialLoad

## Plant-Heat
HVACTemplate:Plant:HotWaterLoop | Unit | Must Have or not | Current Input Value | Note | Comment | Boiler serving HotWaterLoop | HVACTemplate:Plant:Boiler | Unit | Must Have or not | Current Input Value | Note | Comment
Name |  | Y | Hot Water Plant | Name |  |  | Name |  | Y | Boiler 1 | Name
Pump Schedule Name |  |  |  | Pump Control | leave blank if hot water pump is always available |  | Boiler Type |  | Y | HotWaterBoiler | Boiler | DistrictHotWater/ HotWaterBoiler/ CondensingHotWaterBoiler
Pump Control Type |  | Y | Intermittent |  | Intermittent (run if load is sensed) / Continuous |  | Capacity | W | Y | autosize |  | autosie -> based on the peak loads during the design days
Hot Water Plant Operation Scheme Type |  | Y | Default | Operation Scheme | Default (make all equip available at all time) / UserDefined |  | Efficiency |  | Y | 0.8 |  | heating efficiency of the boiler's burner
Hot Water Plant Equipment Operation Schemes Name |  |  |  |  | ignored if previous field is default |  | Fuel Type |  | Y | NaturalGas | Fuel | Electricity/ NaturalGas/ PropaneGas/ FuelOil/, etc
Hot Water Setpoint Schedule Name |  | Y (one of these) |  | Setpoint | ignored if Reset Type is not None |  | Priority |  |  |  | Priority
Hot Water Design Setpoint | C |  | 82 |  | used if previous field blank and Reset Type is None |  | Sizing Factor |  | Y | 1 | Sizing
Hot Water Pump Configuration |  | Y | ConstantFlow | Pump | VariableFlow (simulates a pump with variable flow to boilers and coils) / ConstantFlow |  | Minimum Part Load Ratio |  |  |  | Ratio
Hot Water Pump Rated Head | Pa | Y | 179352 |  |  |  | Maximum Part Load Ratio |  | Y | 1.1
Hot Water Setpoint Reset Type |  | Y | None | Temperature Reset and Setpoint | None/ OutdoorAirTemperatureReset (reset using temperature defined below) |  | Optimum Part Load Ratio |  | Y | 1
Hot Water Setpoint at Outdoor Dry-Bulb Low | C |  | 82.2 |  | all four fields have default values different in IDF-Editor and Manual |  | Water Outlet Upper Temperature Limit | C | Y | 100 | Outlet
Hot Water Reset Outdoor Dry-Bulb Low | C |  | -6.7 |  |  |  | Temperature Plant Loop Type |  |  |  |  | whether serve a HotWaterLoop (default) or MixedWaterLoop
Hot Water Setpoint at Outdoor Dry-Bulb High | C |  | 65.6
Hot Water Reset Outdoor Dry-Bulb High | C |  | 10
Hot Water Pump Type |  | Y | SinglePump | Pump Type
Supply Side Bypass Pipe |  | Y | Yes | Bypass Pipe
Demand Side Bypass Pipe |  | Y | Yes
Fluid Type |  | Y | Water | Fluid | Water/ Ethylene/ Propylene
Loop Design Delta Temperature | deltaC | Y | 11 |  | temperature difference used in sizing the loop flow rate
Maximum Outdoor Dry Bulb Temperature | C |  |  |  | maximum temperature that the loop operates
Load Distribution Scheme |  | Y | SequentialLoad |  | Optimal/ SequentialLoad/ UniformLoad/ SequentialUniformPLR/ UniformPLR

## Plant-Tower
HVACTemplate:Plant:Tower | Unit | Must Have or not | Current Input Value | Comment
Name |  | Y | Tower 1
Tower Type |  | Y | TwoSpeed | SingleSpeed/ TwoSpeed
High Speed Nominal Capacity | W | Y | autosize | autosize -> Low Speed Nominal and Fan Convection also need to be autosized
High Speed Fan Power | W | Y | autosize | fan electric consumption when at high speed
Low Speed Nominal Capacity | W | Y | autosize | applicable only for Tower Type Two Speed
Low Speed Fan Power | W | Y | autosize | fan electric consumption when at low speed
Free Convection Capacity | W | Y | autosize
Priority
Sizing Factor |  | Y | 1
Template Plant Loop Type |  |  |  | ChilledWaterLoop/ MixedWaterLoop